SPECIFICATIONS AND ALLIED TECHNICAL DETAILS OF  CCTV FOR

BHEL - R.C. PURAM – HYDERABAD

| Sl | Technical Specifications and Bill of material | Conformance Yes/ No | Deviation if any |
| --- | --- | --- | --- |
|  | A. Details of CCTV at FACTORY |  |  |
|  | CAMERA High resolution color camera – 29 nos Make: Bosch / ACTI / PELCO/ZICOM/Honeywell or CE/UL approved brands. Specifications as per Annexure “ B “ |  |  |
|  | Outdoor PTZ Cameras with 25X optical zoom with controller–3nos. Make: BOSCH / ACTI / PELCO or CE/UL approved brands Specifications as per Annexure “ C “ |  |  |
|  | 16 channel DVR system (PC based) with software in CD form- 2nos Make: BOSCH / ACTI / PELCO/Zicom/Honeywell or CE/UL approved brands. Specifications as per Annexure “ A “ |  |  |
|  | 20.1” LCD Flat Panel display monitor – 1no Make: BOSCH / ACTI / PELCO /LG / SAMSUNG/HONEYWELL or CE/UL approved brands Specifications as per Annexure “ E “ |  |  |
|  | 21” color Video CRT monitor – 9 nos Make: BOSCH / ACTI / PELCO/HONEYWELL or CE/UL approved brands. Specifications as per Annexure “ D “. 8 nos of CRT will be housed in control panel and 1no will be spare. |  |  |
|  | A suitable sheet metal control panel to house 8 nos of CRT monitor and other hard ware – 1 No. |  |  |
|  | PC work station Make: HP/IBM/DELL - 1no Specifications as per Annexure “ F “ |  |  |
|  | Remote client viewing software – 1no. |  |  |
|  | Online UPS with 1 hour back up with maintenance free batteries – 9nos of 1KVA and 1 no of 5KVA. Make: Libert / APC. Specifications as per Annexure “ G “ |  |  |
|  | Video amplifiers / repeaters / connectors – as required. |  |  |
|  | Supply of cables , RG11, signal and power cables laying in suitable conduits - As required . Please refer lay out as per Annexure “ H“ . |  |  |
|  | Video manager / quad unit Specifications as per Annexure “ I “(If required) Make: Bosch / ACTI / PELCO/ZICOM/Honeywell or CE/UL approved brands. |  |  |
|  | In addition to locating the monitors in the control room at Main Gate , the vendor has to make provision to view any of the 32 cameras on a PC in the office of Assistant Commandant / CISF located at J Gate with password protection Supply of PC, any other hardware and / or software , network components / connectivity required, etc shall be in vendor’s scope. |  |  |
|  | The CCTV system should permit a minimum recording of 14 days of each of the 32 nos. of cameras. |  |  |
|  | The entire CCTV system shall be connected through suitable hard wired cables. The scope includes supply of cables , conduits, laying them, supply of power cables, connecting them, etc . Use of existing Ethernet, remote communication or any other mode is not permitted. |  |  |
|  | The requirement, calls for a complete working system and not components thereof. Bids must be complete with all equipment and required accessories along with necessary power systems including standard Un-interrupted Power Supply for the entire equipment, video connectors, patch connectors, patch leads, mounting and fitting hardware, plugs, sockets, and any hardware/software, supply of cables , laying cables in suitable conduits, necessary excavation, network components, etc. as required for complete installation of the System under this contract. |  |  |
|  | List of cameras, location of cameras and block diagram are all enclosed. |  |  |
|  | Mounting of still cameras: All the 29 nos. of still cameras covered under A-1 above shall be mounted in the existing structures. The scope should include necessary mounting arrangement / brackets / wiring , etc |  |  |
|  | Mounting of 3 nos of PTZ : Each of the PTZ cameras are to be fixed on top of 8m MS hot dip galvanized pole. The scope includes supply , erection and installation, supply of suitable brackets / stands , wiring , necessary civil works, etc, |  |  |
|  | Selection of camera to view on the monitor shall be through PC in the control room. |  |  |
|  | The control room shall be located near the Factory Gate as shown in the layout diagram in annexure “J”. |  |  |
|  | 32 nos of cameras needs to be viewed in 8 nos of monitors i.e. 4 cameras in one monitor. The operator in control room should have the choice of magnifying the view / other selections as desired. To facilitate this , the vendor should include necessary video manager / quad unit as mentioned in point no 12 in his scope |  |  |

Annexure A

16Ch A/V Real time DVR Technical Specifications:

| SL | Details |  |  | Vendor’s acceptance | Remarks |
| --- | --- | --- | --- | --- | --- |
| 1 | Display | Speed | NTSC:480fps, PAL 400fps |  |  |
| 1.1 |  | Screen Division | 1,4,9,16 Division |  |  |
| 2 | Recording | Max. Speed (@CIF) | NTSC:480fps, PAL: 400fps |  |  |
| 2.1 |  | Resolution | NTSC: 704x480, 704x240, 352x240 |  |  |
| 2.2 |  |  | PAL: 704x576, 704x288,352x288 |  |  |
| 2.3 |  | Recording Option | Continuous, Motion, Sensor, Pre-Alarm |  |  |
| 3 | Video | Format | NTSC / PAL |  |  |
| 3.1 |  | CODEC | MPEG4/MJPEG |  |  |
| 3.2 |  | Input | 16CH or more |  |  |
| 3.3 |  | Output | VGA,CVBS, S-Video, Programmable spot out (1Ch quad, 4ch full) |  |  |
| 4 | Audio | Input | 16Ch (line input) |  |  |
| 4.1 |  | Output | 1 Ports/16 Ch |  |  |
| 4.2 |  | CODEC | G.726(8Khz Mono) |  |  |
| 5 | Alarm | Input | 16 Ports |  |  |
| 5.1 |  | Output | 4 Ports or more |  |  |
| 6 | Network | Transmission | Ethernet (RJ45) |  |  |
| 6.1 |  | Protocol | TCP/IP (support Dynamic IP) |  |  |
| 7 | Backup | Device | USB,CD-RW,SCSI, Network,DVD-RW (optional) |  |  |
|  | Search & Export: |  |  |  |  |
|  | It shall be possible to search for recordings in the VRS by camera, date and time. If a data and time is specified, playback shall commence from that date and time. It shall be possible to playback more than one camera simultaneously. |  |  |  |  |
|  | The VR shall be able to export sections of recordings to a separate Windows folder, which can then be written to CD-ROM, DVD-ROM or tape media to be played back at a location not connected to the NVE network. The export process should make available a player application, which can be provided with the exported video. |  |  |  |  |
| 8 | Other Function | Remote Control | Remote Software (CMS) |  |  |
| 8.1 |  | Remote Alarm | Email, CMS Report |  |  |
| 8.2 |  | PTZ | RS 232C/485/Bilinux |  |  |
| 8.3 |  | W/D Function | Yes |  |  |
| 8.4 |  | Image Authentication | Watermark |  |  |
| 8.5 |  | Language | 10 Languages |  |  |
| 8.6 |  | Password | Multi Level User Password Authentication |  |  |
| 8.7 |  | USB | 2 Port (USB 2.0)or more |  |  |
| 9 | Working Temperature | 0 ~ 50 Degrees Centigrade |  |  |  |
| 10 | Power Source | AC 100 ~ 240V, 50/60Hz |  |  |  |

Annexure B

CAMERA SPECIFICATIONS

i) 1/3” HAD CCD in Dome with IR, Built in Back Light Compensation (BLC):

| SL | Details |  | Vendor’s acceptance | Vendor’s remarks |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | Image Sensor | 1/3” HAD CCD |  |  |  |  |
| 2 | Effective Pixels | PAL:500(H) x 582 (V) |  |  |  |  |
| 3 | Signal System | PAL |  |  |  |  |
| 4 | Horizontal Resolution | 480TV Line or more |  |  |  |  |
| 5 | Built in Lens | 3 – 12mm |  |  |  |  |
| 6 | Mini Illumination | 1 Lux |  |  |  |  |
| 7 | Shutter Speed | 1/50 – 1/100000 second |  |  |  |  |
| 8 | S/N Ratio | More than 48db (AGC off) |  |  |  |  |
| 9 | Video Output | 1.0 Vp-p. 75ohms |  |  |  |  |
| 10 | Power Supply | 230V AC |  |  |  |  |
| 11 | Power Consumption | 2.7W or less |  |  |  |  |
| 12 | IR Wavelength | 850nm |  |  |  |  |
| 13 | IR Ray Distance | 30m |  |  |  |  |
| 14 | Infrared Switch | Night/Day ON/OFF |  |  |  |  |
| 15 | Illumination for IR On | Less than 1 Lux |  |  |  |  |

Annexure C

Specification of  PTZ Camera:

| SL | Details | Vendor’s acceptance | Vendor’s remarks |
| --- | --- | --- | --- |
| 1 | High Performance outdoor dome camera with pan tilt and zoom functions. |  |  |
| 2 | 1/3-inch Hi-Resolution CCD with 420/460/480 TVL . |  |  |
| 3 | Day and Night Operation with 25x Optical Zoom Lens (3.8 mm to 95 mm) and 10x Electronic Zoom. |  |  |
| 4 | FPS : 30fps |  |  |
| 5 | Day and Night Operation with Mechanical IR Cut Filter: |  |  |
| 6 | Mini Illumination - 1 Lux |  |  |
| 7 | ON/OFF, Auto, Alarm, Timer |  |  |
| 8 | Pan: 360° unLimited Rotation ; Tilt: -5deg to 90deg |  |  |
| 9 | Power Supply – 230VAC |  |  |
| 10 | 99 prepositions or more |  |  |
| 11 | Suitable for Indoor / Outdoor centralized monitoring setup |  |  |
| 24 | Software Upgrade: Onsite SW Upgrade |  |  |
| 25 | Power line Surge Protection and Lightning Protection : Built In |  |  |

Annexure D

CRT Monitor Specifications:

| Details |  |  |  | Vendor’s acceptance | Vendor’s remarks |
| --- | --- | --- | --- | --- | --- |
| CDT | Size/Viewable Area |  | 21"(20.0" Viewable) |  |  |
|  | Display Size | Typical | 393x295 |  |  |
|  |  | Max | 406.4x304.8 |  |  |
|  | Pitch |  | 0.20mm(H) |  |  |
|  | Deflection |  | 90' |  |  |
|  | Surface treatment |  | Multi-Layer Coating |  |  |
| Signal Input | Video Signal |  | RGB Analog |  |  |
|  | Sync Signal |  | Separate H/V, Composite, SOG |  |  |
|  | Connection |  | 15pin D-Sub, 5BNC |  |  |
|  | Cable |  | VGA Cable |  |  |
|  | Frequency | Horizontal | 15~130kHz |  |  |
|  |  | Vertical | 50~160Hz |  |  |
|  |  | Pixel | 360MHz |  |  |
| Resolution | Maximum |  | 2048x1536 @80Hz |  |  |
|  | Recommended |  | 1280x1024 @118Hz 1600x1200 @102Hz |  |  |
| Features | Plug & Play |  | DDC 2B/2Bi/GTF |  |  |
|  | User Control(OSD) | Display Directorx2122 | Available |  |  |
|  | Mode | Factory/User | 8/10 modes |  |  |
|  | Cabinet Color (front / back) |  | Black/Silver-Tone |  |  |
|  | Environmental /Ergonomics |  | TCO 03 |  |  |
| Regulation | Windows Logo |  | Windows 98/2000/ME/XP |  |  |
|  | Power Supply |  | AC90~264VAC, 50/60Hz |  |  |
| Power | Power Consumption |  | 130W |  |  |
|  | Stand By Power (DPMS) |  | ≤2W @Off Stateu |  |  |
|  | Regulation |  | EPA/Energy2000/VESA DPMS |  |  |

Annexure E

TFT / LCD Monitor Specifications:

| Details |  |  | Vendor’s acceptance | Vendor’s remarks |
| --- | --- | --- | --- | --- |
| PANEL | Viewable Area | 19" |  |  |
|  | Pixel Pitch | 0.255 x 0.255 mm |  |  |
|  | Brightness | 250 cd/m2 |  |  |
|  | Contrast Ratio | 500:1 |  |  |
|  | Viewing Angle(H/V) | 170o / 170o |  |  |
|  | Response Time | 16 ms |  |  |
|  | Interface | Analog / Digital |  |  |
| FREQUENCY | Horizontal Frequency | 30~81 kHz |  |  |
|  | Vertical Frequency | 56~75 Hz |  |  |
|  | Bandwidth | 162 MHz |  |  |
| MAXIMUM RESOLUTION |  | 500 TVL |  |  |
| COLOR SUPPORTED |  | 16 Mil. Or more |  |  |
| SIGNAL INPUT | Input Video Signal | Composite video A , B |  |  |
|  | Video Level | Analog : 0.7VP-P, Digital : TMDSTM |  |  |
|  | Sync. Type | Separate H/V, Composite H/V, SOG |  |  |
|  | Audio input | 2 input RCA jack |  |  |
|  | Input Connectors | 15pin D-Sub, DVI-D |  |  |
|  | Signal Cables | VGA Cable, DVI Cable |  |  |
|  |  | DDC 2B |  |  |
| Signal output | video | Composite video A , B |  |  |
|  | Audio | 2 outputs RCA jack |  |  |
|  | DDC | 63 Watts (Max.) |  |  |
| POWER | DPMS Mode | <2 Watt |  |  |
|  | Power Off Mode | <0 Watt (Mechanical Switch-Power off) |  |  |
|  | Energy Star/NUTEK | O |  |  |
|  | O |  |  |  |
| OSD-DIGITAL DISPLAY DIRECTOR™ |  | VESA 100mm |  |  |
| WALL-MOUNT |  | TCO'03(Silver)/ TCO’99(Black) |  |  |
| EMISSIONS STANDARD |  | Silver / Silver |  |  |
| CABINET COLOR |  | Black |  |  |
| AVAILABLE COLORS (OPTIONAL) |  | O |  |  |
| MAC COMPATIBILITY |  | Built-in Power, Dual interface, Narrow Bezel, Mechanical S/W, Pivot & HAS Stand (100mm Lift). |  |  |

Annexure F

Specification of PC

| - 7.1 | CPU Single Intel Xeon 3 GHz or better chipset with 1 MB cache, Hyper-Threading Technology and Intel Extended Memory 64 Technology (EM64T). Intel High Performance E7520 Chipset with 800 MHz FSB or better. |  |  |
| --- | --- | --- | --- |
| - 7.2 | HDD Interface IDE or better |  |  |
| - 7.3 | RAM Up to 1 GB ECC DDR2 SDRAM, 400 MHz (2x512 MB) – 6 DIM Socket OS Microsoft Windows XPP with latest service pack |  |  |
| - 7.4 | Ethernet Card Dual Onboard Intel Gigabit Ethernet with Load Balancing and Fail over Support |  |  |
| - 7.5 | CD Drive 24x EIDE CD-ROM |  |  |
| - 7.6 | HDD 160 GB SCSI HDD, 10,000 U/Min, 1” S.M.A.R.T.II or better |  |  |
| - 7.7 | Other features Onboard Single channel Ultra 320 SCSI Controller Hot-plug HDD, redundant Hot-plug fan. 1 internal Hot-plug SCSI HDD 1 U mounting |  |  |

Annexure G

ONLINE UPS

| 1 | 1KVA with 1 hour at each gate totaling 9 nos from Libert / APC with SMF |  |  |
| --- | --- | --- | --- |
| 2 | 5KVA with 1 hour back up at control room – from Libert /APC with SMF |  |  |
| 3 | Supply of suitable cables , plugs , etc from / to UPS are in vendor’s scope |  |  |

Annexure H

Cable and  connectors

| 1 | Supply of all cables ( control , power, etc) , necessary PVC conduits, laying of cables (including digging and proper filling thereafter), civil works, etc , are all in vendor’s scope . Please refer LAY OUT diagram in Annexure ‘J’ for reference. |  |  |
| --- | --- | --- | --- |
| 2 | All the cables ( signal & power) shall be armoured. |  |  |

Annexure I

QUAD Unit

| 1 | Power - 90 to 265 VAC Video format - PAL Resolution - 720 x 620 Video input - 4 Video output - Loop through (4) - 1 Monitor output Video input voltage - 2 VP-P max Camera selection - Quad/Fullscreen/Sequencing |  |  |
| --- | --- | --- | --- |

ANNEXURE “J”.   BHEL SITE LAY OUT DIAGRAM.

Annexure K

DETAILS OF CAMERAS

A. The number / type  of cameras for each of the gates are as below:

| SL | GATE | Fixed camera with varifocal lens | Outdoor P/T/Z Camera with 25 X optical Zoom | Sub Total |
| --- | --- | --- | --- | --- |
| 1 | Switch gear | 2 | 0 | 2 |
| 2 | J gate | 5 | 1 | 6 |
| 3 | Factory gate | 7 | 1 | 8 |
| 4 | C gate | 2 | 0 | 2 |
| 5 | MIG gate | 2 | 0 | 2 |
| 6 | Admn 1 | 2 | 1 | 3 |
| 7 | Admn 2 | 2 | 0 | 2 |
| 8 | K Gate | 2 | 0 | 2 |
| 9 | Rail gate | 1 | 0 | 1 |
| 10 | Spare | 4 | 0 | 4 |
|  | GRAND TOTAL | 29 | 3 | 32 |

Admn 1 : Administrative Building gate 1.

Admn 2 : Administrative Building gate 2.